## FPC-CT 10W WITH PLUG
TEST CERTIFICATE
Customer : M/s.Warmup GmbH
PO No : PODE11057 | [5 empty] | ORIGINAL
PO Dt : 05.02.2026 | [5 empty] | S.NO : FPC-Wup-36
Product : Freeze Protection Cable (FPC-CT), 10W/m | [5 empty] | DATE : 13.03.2026
Mode of shipment : By Sea
Sl. | CABLE | LENGTH | NOMINAL POWER | CABLE | BETWEEN METAL SHEATH TO CONDUCTOR
No. | Sl.No. | (in Mtrs) | at 230 V | RESISTANCE | H.V.Test at 2.0 KV | I.R.After H.V.Test with
|  |  | (WATT) | (in Ohms) | AC for 60 Sec | 500V DC Tester (in MΩ)
1 | 07904E | 2 | 20 | 2696.6 | No Breakdown | > 100
2 | 18758A | 2 | 20 | 2694.7 | No Breakdown | > 100
3 | 18764A | 2 | 20 | 2683.3 | No Breakdown | > 100
4 | 30698A | 2 | 20 | 2696.6 | No Breakdown | > 100
5 | 30700A | 2 | 20 | 2694.7 | No Breakdown | > 100
6 | 30701A | 2 | 20 | 2683.3 | No Breakdown | > 100
7 | 30729A | 2 | 20 | 2681.2 | No Breakdown | > 100
8 | 36034H | 2 | 20 | 2698.5 | No Breakdown | > 100
9 | 36035H | 2 | 20 | 2703.4 | No Breakdown | > 100
10 | 36036H | 2 | 20 | 2701.2 | No Breakdown | > 100
11 | 36037H | 2 | 20 | 2670.7 | No Breakdown | > 100
12 | 36038H | 2 | 20 | 2703.96 | No Breakdown | > 100
13 | 36039H | 2 | 20 | 2686.1 | No Breakdown | > 100
14 | 36040H | 2 | 20 | 2683.5 | No Breakdown | > 100
15 | 36041H | 2 | 20 | 2685.2 | No Breakdown | > 100
16 | 36043H | 2 | 20 | 2683.9 | No Breakdown | > 100
17 | 36044H | 2 | 20 | 2612.7 | No Breakdown | > 100
18 | 36045H | 2 | 20 | 2692.4 | No Breakdown | > 100
19 | 36046H | 2 | 20 | 2688 | No Breakdown | > 100
20 | 36048H | 2 | 20 | 2676.5 | No Breakdown | > 100
21 | 36049H | 2 | 20 | 2674.6 | No Breakdown | > 100
22 | 36051H | 2 | 20 | 2630.9 | No Breakdown | > 100
23 | 36052H | 2 | 20 | 2674 | No Breakdown | > 100
24 | 36053H | 2 | 20 | 2692.8 | No Breakdown | > 100
25 | 36054H | 2 | 20 | 2669.7 | No Breakdown | > 100
26 | 36055H | 2 | 20 | 2749.4 | No Breakdown | > 100
27 | 36056H | 2 | 20 | 2751.4 | No Breakdown | > 100
28 | 36057H | 2 | 20 | 2722.2 | No Breakdown | > 100
29 | 36058H | 2 | 20 | 2784.3 | No Breakdown | > 100
30 | 36059H | 2 | 20 | 2721.5 | No Breakdown | > 100
31 | 36060H | 2 | 20 | 2747.8 | No Breakdown | > 100
32 | 36061H | 2 | 20 | 2741 | No Breakdown | > 100
33 | 36062H | 2 | 20 | 2692.3 | No Breakdown | > 100
34 | 36063H | 2 | 20 | 2736.2 | No Breakdown | > 100
35 | 36064H | 2 | 20 | 2714.4 | No Breakdown | > 100
36 | 36066H | 2 | 20 | 2782.8 | No Breakdown | > 100
37 | 36069H | 2 | 20 | 2766.6 | No Breakdown | > 100
38 | 36070H | 2 | 20 | 2777.8 | No Breakdown | > 100
39 | 36071H | 2 | 20 | 2736.8 | No Breakdown | > 100
40 | 36072H | 2 | 20 | 2650.2 | No Breakdown | > 100
1 | 36076H | 4 | 40 | 1351.5 | No Breakdown | > 100
2 | 36077H | 4 | 40 | 1354.6 | No Breakdown | > 100
3 | 36078H | 4 | 40 | 1356.9 | No Breakdown | > 100
4 | 36079H | 4 | 40 | 1353.5 | No Breakdown | > 100
5 | 36080H | 4 | 40 | 1343.4 | No Breakdown | > 100
6 | 36081H | 4 | 40 | 1328.1 | No Breakdown | > 100
7 | 36082H | 4 | 40 | 1350.1 | No Breakdown | > 100
8 | 36083H | 4 | 40 | 1356.2 | No Breakdown | > 100
9 | 36084H | 4 | 40 | 1354.8 | No Breakdown | > 100
10 | 36085H | 4 | 40 | 1346.8 | No Breakdown | > 100
1 | 18740A | 6 | 60 | 878.1 | No Breakdown | > 100
2 | 36087H | 6 | 60 | 878.1 | No Breakdown | > 100
3 | 36088H | 6 | 60 | 885.3 | No Breakdown | > 100
4 | 36090H | 6 | 60 | 891.1 | No Breakdown | > 100
5 | 36091H | 6 | 60 | 888.6 | No Breakdown | > 100
6 | 36092H | 6 | 60 | 889.2 | No Breakdown | > 100
7 | 36093H | 6 | 60 | 891.1 | No Breakdown | > 100
8 | 36094H | 6 | 60 | 891 | No Breakdown | > 100
9 | 36095H | 6 | 60 | 889.1 | No Breakdown | > 100
10 | 36096H | 6 | 60 | 890.8 | No Breakdown | > 100
11 | 36098H | 6 | 60 | 890.2 | No Breakdown | > 100
12 | 36099H | 6 | 60 | 884.9 | No Breakdown | > 100
13 | 36100H | 6 | 60 | 891.8 | No Breakdown | > 100
14 | 36101H | 6 | 60 | 885.2 | No Breakdown | > 100
15 | 36102H | 6 | 60 | 874.3 | No Breakdown | > 100
16 | 36103H | 6 | 60 | 890.8 | No Breakdown | > 100
17 | 36104H | 6 | 60 | 891.3 | No Breakdown | > 100
18 | 36105H | 6 | 60 | 892.3 | No Breakdown | > 100
19 | 36106H | 6 | 60 | 891.1 | No Breakdown | > 100
20 | 36107H | 6 | 60 | 883.5 | No Breakdown | > 100
21 | 36108H | 6 | 60 | 886.6 | No Breakdown | > 100
22 | 36109H | 6 | 60 | 884.1 | No Breakdown | > 100
23 | 36110H | 6 | 60 | 885.6 | No Breakdown | > 100
24 | 36111H | 6 | 60 | 889.72 | No Breakdown | > 100
25 | 36112H | 6 | 60 | 880.22 | No Breakdown | > 100
26 | 36113H | 6 | 60 | 890.3 | No Breakdown | > 100
27 | 38765T | 6 | 60 | 885.6 | No Breakdown | > 100
28 | 38773T | 6 | 60 | 889.72 | No Breakdown | > 100
29 | 81669D | 6 | 60 | 880.22 | No Breakdown | > 100
30 | 87165H | 6 | 60 | 890.3 | No Breakdown | > 100
1 | 36118H | 14 | 140 | 382.3 | No Breakdown | > 100
2 | 36119H | 14 | 140 | 382.49 | No Breakdown | > 100
3 | 36120H | 14 | 140 | 382.3 | No Breakdown | > 100
4 | 36121H | 14 | 140 | 382.4 | No Breakdown | > 100
5 | 36122H | 14 | 140 | 382.2 | No Breakdown | > 100
6 | 36123H | 14 | 140 | 382.2 | No Breakdown | > 100
7 | 36124H | 14 | 140 | 382.64 | No Breakdown | > 100
8 | 36125H | 14 | 140 | 383.3 | No Breakdown | > 100
9 | 36127H | 14 | 140 | 382.3 | No Breakdown | > 100
10 | 36128H | 14 | 140 | 380 | No Breakdown | > 100
for THERMOPADS PVT LTD
CHECKED BY |  |  |  |  | APPROVED BY