## 5.05W
TEST CERTIFICATE
Customer : M/s. Warmup
PO No : PO27805 | [5 empty] | ORIGINAL
PO Dt : 05.02.2026 | [5 empty] | S.No : UTHCT-Wup-29
Product : UTHC-T, 5.05 W/m(DCM-C) | [5 empty] | DATE : 21.03.2026
Mode of shipment : By Sea
Sl. | CABLE | LENGTH | NOMINAL POWER | CABLE RESISTANCE | IR VALUE | HIGH VOLTAGE TEST
No. | Sl.No. | (In Mtrs) | at 230 V | (in Ohms) | (in MEGA OHMS) | AT 3 KV FOR 60 SEC.
|  |  | (WATT) | (at 20degC)
1 | 00185573D | 21.8 | 110 | 478.9013 | > 500 | No Breakdown
2 | 00185574D | 21.8 | 110 | 478.8873 | > 500 | No Breakdown
3 | 00185575D | 21.8 | 110 | 478.1084 | > 500 | No Breakdown
4 | 00185577D | 21.8 | 110 | 479.8011 | > 500 | No Breakdown
5 | 00185579D | 21.8 | 110 | 479.368 | > 500 | No Breakdown
6 | 00185580D | 21.8 | 110 | 478.422 | > 500 | No Breakdown
7 | 00185581D | 21.8 | 110 | 479.5063 | > 500 | No Breakdown
8 | 00185582D | 21.8 | 110 | 478.7055 | > 500 | No Breakdown
9 | 00185583D | 21.8 | 110 | 479.5063 | > 500 | No Breakdown
10 | 00185584D | 21.8 | 110 | 478.7055 | > 500 | No Breakdown
11 | 00185589D | 21.8 | 110 | 479.3851 | > 500 | No Breakdown
12 | 00185590D | 21.8 | 110 | 478.3471 | > 500 | No Breakdown
13 | 00185591D | 21.8 | 110 | 479.663 | > 500 | No Breakdown
14 | 00185592D | 21.8 | 110 | 479.704 | > 500 | No Breakdown
15 | 00185593D | 21.8 | 110 | 476.0593 | > 500 | No Breakdown
16 | 00185594D | 21.8 | 110 | 479.5393 | > 500 | No Breakdown
17 | 00185595D | 21.8 | 110 | 478.3504 | > 500 | No Breakdown
18 | 00185596D | 21.8 | 110 | 479.4144 | > 500 | No Breakdown
1 | 00153591D | 130.6 | 660 | 77.438 | > 500 | No Breakdown
2 | 00153593D | 130.6 | 660 | 78.0536 | > 500 | No Breakdown
3 | 00153594D | 130.6 | 660 | 77.5967 | > 500 | No Breakdown
4 | 00153595D | 130.6 | 660 | 77.8063 | > 500 | No Breakdown
5 | 00153596D | 130.6 | 660 | 77.5383 | > 500 | No Breakdown
6 | 00153597D | 130.6 | 660 | 77.8989 | > 500 | No Breakdown
7 | 00167724D | 130.6 | 660 | 77.8989 | > 500 | No Breakdown
8 | 00185598D | 130.6 | 660 | 79.1397 | > 500 | No Breakdown
9 | 00185599D | 130.6 | 660 | 79.1457 | > 500 | No Breakdown
10 | 00185600D | 130.6 | 660 | 79.1857 | > 500 | No Breakdown
11 | 00185603D | 130.6 | 660 | 79.099 | > 500 | No Breakdown
12 | 00185605D | 130.6 | 660 | 79.0724 | > 500 | No Breakdown
13 | 00185606D | 130.6 | 660 | 79.073 | > 500 | No Breakdown
14 | 00185609D | 130.6 | 660 | 79.3192 | > 500 | No Breakdown
15 | 00185611D | 130.6 | 660 | 79.1563 | > 500 | No Breakdown
16 | 00185612D | 130.6 | 660 | 79.4055 | > 500 | No Breakdown
for THERMOPADS PVT LTD
CHECKED BY |  |  |  |  | APPROVED BY